## System Fault Summary
System Fault Summary
No. | Fault Type | Fault Name | Fault Code | Corresponding LC Actions | Risk Analysis | Remarks
1 | Alarm | BMS Communication Loss |  | ① Enable alarm light ② Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shutdown, trip the AC side. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. |  | LC clears BMS data to all 0. | PCS shuts down due to a fault, and MPPT shuts down synchronously.
2 |  | PCS communication loss |  | ① Alarm light on, operation light off ② 15s timeout protection; PCS will shut down automatically (need to be in LC save mode). |  | LC clears PCS data to all 0.
3 |  | AC air conditioner communication lost |  | ① Enable alarm light ② Inverter phase voltage is greater than 220V and air conditioner communication lost is for 5 minutes; if grid-connected/off-grid switching occurs, restart the 5-minute timer. Send PCS shutdown; if 0.1kW is fed to the grid for more than 6s after PCS shutdown, trip the AC side. ③ If the output is shut down but the absolute value of the DC side current is greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. | LC clears AC data to all 0. If the air conditioner is in operation state and communication is lost, the air conditioner operates independently according to the parameters configured by the LC. BMS limits power based on temperature.
4 |  | Customer-selected electricity meter communication lost |  | ① Operation light on, fault light on |  | LC clears electricity meter 1 data to all 0.
5 |  | Auxiliary electricity meter communication lost |  | ① Operation light on, fault light on |  | LC clears electricity meter 2 data to all 0.
6 |  | Transformer electricity meter communication lost |  | ① Enable alarm light ② In grid-connected mode, send PCS shutdown. If there is still 0.1kW feeding to the grid for more than 6s after PCS shutdown, trip the AC side. ③ In grid-connected mode, after a fault occurs, if the output is shut down but the absolute value of the DC side current is greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. |  | No judgment in off-grid scenario
7 |  | Temperature and humidity sensor communication lost |  | ① Enable alarm light |  | LC clears temperature and humidity sensor data to all 0. Temperature and humidity sensors are placed in the electrical compartment, and high temperature and high humidity alarms need to be added. Consider adding risk warnings based on the dew point meter.
8 |  | QF1 control failure |  | ① Enable alarm light and remote alarm signal ② Disconnect QF2 |  | If both QF1 and QF2 control fail, since PCS will be controlled to shut down, the risk is controllable. However, if PCS communication also fails, PCS must apply extreme protection to the battery information reported by BMS.
9 |  | QF2 control failure |  | ① Enable alarm light and remote alarm signal ② Disconnect QF1
10 |  | Solid state drive mounting lost |  | ① Operation light on, fault light on |  | Activity event reminder
11 |  | 4G Module Mounting Loss |  | ① Operation light on, fault light on |  | Activity event reminder
12 |  | Abnormal loss of historical database |  | ① Operation light on, fault light on |  | Activity event reminder
13 |  | CPU core 1 temperature abnormal |  | ① Alarm light on, operation light off. ② Send PCS shutdown. |  | Chip temperature exceeds 105°C, causing crash; fault trigger temperature is 100°C.
14 |  | CPU core 2 temperature abnormal |  | ① Operation light on, fault light on ② Send PCS shutdown. |  | Activity event reminder
15 |  | CPU core 3 temperature abnormal |  | ① Operation light on, fault light on ② Send PCS shutdown. |  | Activity event reminder
16 |  | Dehumidifier communication lost |  | ① Operation light on, fault light on
17 |  | Dehumidifier alarm |  | ① Operation light on, fault light on
18 |  | Electrical Compartment Access Control |  | ① Alarm light on, operation light on
19 |  | Carbon monoxide sensor communication lost |  | ① Operation light on, fault light on
20 |  | IO board communication lost |  | ① Enable alarm light ② Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shutdown, trip the AC side. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
21 |  | MPPT communication loss |  | ① Alarm light on, operation light off
22 |  | Inverter LCD panel communication lost |  | ① Operation light on, fault light on
23 | Protection | PCS and battery wiring abnormal |  | ① Enable alarm light ② Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shutdown, trip the AC side. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. |  | G230 single cluster, not needed
24 |  | Emergency stop feedback |  | ① Alarm light on, operation light off ② PCS shutdown ③ Air conditioner shutdown ④ QF1, QF2 trip
25 |  | Water Infiltration Feedback |  | ① Alarm light on, operation light off ② Remote emergency stop output ③ PCS shutdown ④ Air conditioner shutdown ⑤ QF1, QF2 trip
26 |  | Battery Compartment Aerosol Feedback |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ Remote emergency stop output ⑤ PCS shutdown ⑥ Air conditioner shutdown ⑦ QF1, QF2 trip ⑧ STS cabinet grid circuit breaker trip, STS cabinet generator circuit breaker trip
27 |  | Battery Compartment Access Control |  | ① Alarm light on, operation light off ② Stop the exhaust fan and exhaust valve. ③ PCS shutdown ④ Air conditioner shutdown
28 |  | Low Gas Alarm Low gas alarm (concentration > 8%) |  | ① Alarm light on, operation light on ② Exhaust fan and exhaust valve start.
29 |  | High Gas Alarm High gas alarm (concentration > 20%) |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ Remote emergency stop output ⑤ PCS shutdown ⑥ Air conditioner shutdown ⑦ QF1, QF2 trip
30 |  | Electrical compartment aerosol feedback |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ Remote emergency stop output ⑤ PCS shutdown ⑥ Air conditioner shutdown ⑦ QF1, QF2 trip ⑧ STS cabinet grid circuit breaker trip, STS cabinet generator circuit breaker trip
31 |  | Temperature Sensing Feedback |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ PCS shutdown ⑤ Air conditioner shutdown
32 |  | Smoke Sensing Feedback |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ PCS shutdown ⑤ Air conditioner shutdown
33 |  | Lightning protection signal feedback |  | ① Alarm light on, operation light off
34 |  | Fire alarm (temperature sensor + smoke sensor) |  | ① Alarm light on, operation light off ② Exhaust fan and exhaust valve start. ③ Audio-visual start ④ Remote emergency stop output ⑤ Aerosol spray ⑥ PCS shutdown ⑦ Air conditioner shutdown ⑧ QF1, QF2 trip ⑨ STS cabinet grid circuit breaker trip, STS cabinet generator circuit breaker trip
35 |  | PCS startup failure |  | ① Alarm light on, operation light off
36 |  | Fire alarm control panel action process |  | ① Enable the fire alarm control panel function. ② Smoke or temperature triggers: LC reports to the fire alarm control panel via IO board DO2 (temperature sensor) and DO3 (smoke sensor). A single smoke or temperature trigger will cause the fire alarm control panel to alarm. ③ When the fire alarm control panel detects both smoke and temperature triggers, it starts executing the audio-visual alarm and aerosol spray. ④ If the fire alarm control panel does not respond within 30s (IO board DI3 (audio-visual input) and DI4 (aerosol input) input are low level), it is considered not triggered, and LC will perform the action after 30s. ⑤ If the fire alarm control panel function is not enabled, LC will execute based on the normal logic.
37 |  | STS communication loss |  | ① Operation light on, fault light on.
38 |  | STS cabinet dehumidifier communication lost |  | ① Operation light on, fault light on.
39 |  | STS cabinet IO board communication lost |  | ① Operation light on, fault light on.
40 |  | STS cabinet electricity meter communication lost |  | ① Operation light on, fault light on.
41 |  | STS cabinet IO board enters manual control mode |  | ① Operation light on, fault light on.
42 |  | STS cabinet grid circuit breaker trip |  | ① Operation light on, fault light on.
43 |  | STS cabinet generator circuit breaker trip |  | ① Operation light on, fault light on.
44 |  | STS cabinet lightning protection alarm |  | ① Operation light on, fault light on.
45 |  | EMS fire fault (Smoke sensor + temperature sensor, battery pack, battery compartment, electrical compartment aerosol spray) |  | ① Enable alarm light ② QF1, QF2 trip ③ Air conditioner shutdown ④ PCS, MPPT shutdown
46 |  | EMS remote emergency stop (External input) |  | ① Enable alarm light ② PCS, MPPT shutdown ③ Air conditioner shutdown
47 |  | EMS STS communication lost |  | ① Enable alarm light ② The PCS is currently fault-free and has remained so for 5 minutes, only then can it be determined that the PCS and MPPT have shut down.
48 |  | EMS STS cabinet electricity meter communication lost |  | /
49 |  | EMS STS cabinet IO board communication lost |  | /
50 |  | EMS STS cabinet dehumidifier communication lost |  | /
51 |  | EMS diesel generator communication lost |  | /
52 |  | EMS grid signal feedback |  | /
53 |  | EMS diesel generator feedback |  | /
54 |  | EMS lightning protection module alarm |  | /
55 |  | EMS solid state drive mounting lost |  | ① Enable alarm light ② PCS, MPPT shutdown
56 |  | EMS 4G module mounting lost |  | ① Enable alarm light ② PCS, MPPT shutdown
57 |  | Abnormal loss of EMS historical database |  | ① Enable alarm light ② PCS, MPPT shutdown
58 |  | EMS CPU core 1 temperature abnormal |  | ① Enable alarm light ② PCS, MPPT shutdown
59 |  | EMS CPU core 2 temperature abnormal |  | ① Enable alarm light ② PCS, MPPT shutdown
60 |  | EMS CPU core 3 temperature abnormal |  | ① Enable alarm light ② PCS, MPPT shutdown

## BMS Fault Summary
BMS Fault Summary
No. | Fault Type | Fault Name | Corresponding BMS Actions | Corresponding LC Actions | Remarks
1 | Protection | Cell undervoltage protection | ① Set the discharge limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a discharge fault occurs and LC controls BMS to shield the discharge fault for charging preparation, trigger trip protection if discharge current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | PCS will still draw power from the DC side after shutdown. Pay special attention to power consumption under PCS shutdown conditions to prevent battery over-discharge.
2 |  | Total undervoltage protection | ① Set the discharge limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a discharge fault occurs and LC controls BMS to shield the discharge fault for charging preparation, trigger trip protection if discharge current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | PCS will still draw power from the DC side after shutdown. Pay special attention to power consumption under PCS shutdown conditions to prevent battery over-discharge.
3 |  | Cell overvoltage protection | ① Set the charging limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a charging fault occurs and LC controls BMS to shield the charging fault for discharging preparation, trigger trip protection if the charging current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | PCS shutdown condition added: BMS detects current greater than 2A. Trip condition added: BMS detects current greater than 0A.
4 |  | Total overvoltage protection | ① Set the charging limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a charging fault occurs and LC controls BMS to shield the charging fault for discharging preparation, trigger trip protection if the charging current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | PCS shuts down due to a fault, and MPPT shuts down synchronously.
5 |  | Charging overtemperature protection | ① Set the charging limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a charging fault occurs and LC controls BMS to shield the charging fault for discharging preparation, trigger trip protection if the charging current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | ② After a fault occurs, if the output is shut down but the DC-side current remains non-zero for a cumulative duration exceeding 3s, disconnect the DC circuit breaker. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
6 |  | Discharging overtemperature protection | ① Set the discharge limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. Use accumulation decrement, no reset. ③ If a discharge fault occurs and LC controls BMS to shield the discharge fault for charging preparation, trigger trip protection if discharge current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
7 |  | Charging overcurrent protection | ① Set the charging limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a charging fault occurs and LC controls BMS to shield the charging fault for discharging preparation, trigger trip protection if the charging current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
8 |  | Discharge overcurrent protection | ① Set the discharge limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. Use accumulation decrement, no reset. ③ If a discharge fault occurs and LC controls BMS to shield the discharge fault for charging preparation, trigger trip protection if discharge current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
9 |  | Charging low temperature protection | ① Set the charging limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ If a charging fault occurs and LC controls BMS to shield the charging fault for discharging preparation, trigger trip protection if the charging current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
0.1 |  | Discharge low temperature protection | ① Set the discharge limit current to 0, send a shutdown command to PCS via PCS CAN, and enable PCS shutdown via the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. Use accumulation decrement, no reset. ③ If a discharge fault occurs and LC controls BMS to shield the discharge fault for charging preparation, trigger trip protection if discharge current is detected as below 1A for 10s, 1-2A for 5s, or above 2A for 2s. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
0.10.1 |  | Excessive differential pressure protection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | 800mV
0.12 |  | Excessive temperature difference protection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | 0.15°C
0.13 |  | BMS power connector overtemperature protection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② After a fault occurs, if the output is shut down but the DC-side current remains non-zero for a cumulative duration exceeding 5s, disconnect the DC circuit breaker. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | G230 does not have this fault.
0.14 |  | BMU power connector overtemperature protection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ The fault needs to be manually cleared. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side. | Confirm the absolute temperature with the testing department, and modify the configuration based on test results before shipment. The provisional value is set at 70°C.
0.15 |  | Insulation fault | ① Set the charging and discharge limit current to 0. ② Output DO to shut down PCS. ③ When LC communication loss fault is triggered, disconnect the DC circuit breaker. | ① Enable alarm light ② Send PCS shutdown. ③ Disconnect the DC circuit breaker.
0.16 |  | Power supply voltage abnormal protection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
0.17 |  | Internal Total Voltage Acquisition Fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
0.18 |  | Fuse total voltage acquisition fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
0.19 |  | PCS total voltage acquisition fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
20 |  | Heating total voltage acquisition fault | / | ① Enable alarm light | G230 does not have this fault. Should this type be moved to alarm? Modify TCP protocol?
20.1 |  | Battery cell voltage acquisition disconnection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
22 |  | Battery cell temperature acquisition disconnection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
23 |  | Current acquisition fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
24 |  | Current module fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
25 |  | Main positive relay sticking fault | / | ① Enable alarm light | G230 does not have this fault.
26 |  | Charging relay sticking fault | / | ① Enable alarm light | G230 does not have this fault.
27 |  | Discharge relay sticking fault | / | ① Enable alarm light | G230 does not have this fault.
28 |  | Precharging relay sticking fault | / | ① Enable alarm light | G230 does not have this fault.
29 |  | Heating relay sticking fault | / | ① Enable alarm light | G230 does not have this fault.
30 |  | EEPROM fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
30.1 |  | RTC clock fault | / | / | Move to alarm.
32 |  | Precharging failure fault | ① Set charging and discharge limit current to 0, and send a shutdown command to PCS via PCS CAN. ② If the output is shut down but the current remains non-zero for a cumulative duration exceeding 5s, and the LC communication loss fault is triggered, disconnect the DC circuit breaker. | ① Enable alarm light ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
33 |  | Main positive relay drive failure fault | / | ① Enable alarm light | G230 does not have this fault.
34 |  | Charging relay drive failure fault | / | ① Enable alarm light | G230 does not have this fault.
35 |  | Discharge relay drive failure fault | / | ① Enable alarm light | G230 does not have this fault.
36 |  | Precharging relay drive failure fault | / | ① Enable alarm light | G230 does not have this fault.
37 |  | Heating relay drive failure fault | / | ① Enable alarm light | G230 does not have this fault.
38 |  | BMU quantity abnormal fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
39 |  | BMU communication loss fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
40 |  | Blown fuse fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown, if there is still power greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
40.1 |  | BMS address duplication fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown, if there is still power greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
42 |  | BMU address duplication fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
43 |  | PCS communication failure fault | / | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
44 |  | BMS communication loss fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
45 |  | Limit protection | ① Set the charging and discharge limit current to 0. ② Output DO to shut down PCS. ③ Self-recovery is not allowed; disconnect the DC circuit breaker when LC communication loss fault is triggered. | ① Enable alarm light ② Send PCS shutdown. ③ Disconnect the DC circuit breaker. | If the DC circuit breaker trips abnormally, the battery power will be
46 |  | BMS power plug-in temperature acquisition disconnection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker. | G230 does not have this fault.
47 |  | BMU power plug-in temperature acquisition disconnection | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Receive BMS forced trip command and disconnect the DC circuit breaker; LC implements DC trip protection on the PCS DC-side current using a stepwise approach: 2A for 5s and 5A for 2s. Use accumulation decrement, no reset. ③ After PCS shutdown, if there is 0.1kW feeding to the grid for more than 6s, trip the AC side.
48 |  | Battery cell abnormal fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light and remote alarm signal | G230 does not have this fault.
49 |  | Fire protection feedback (aerosol spray) fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. ③ Pack fan shutdown | ① Same as battery compartment aerosol spray | All fire protection faults at BMU level, BMS level, and LC level are modified to non-recoverable faults, and the same handling strategy as system aerosol spray is applied.
50 |  | LC Communication Loss | / | /
50.1 |  | BMU AFE communication failure fault | ① Set the charging and discharge limit current to 0, send a shutdown command to PCS through PCS CAN, and enable PCS shutdown through the dry contact. ② If there is still current after controlling PCS to shut down, perform trip protection based on the following thresholds: below 1A for 10s, 1-2A for 5s, and above 2A for 2s. (If communication with LC is available, instruct LC whether to trip; if communication with LC is lost, control circuit breaker trip independently.) Use accumulation decrement, no reset. | ① Enable alarm light ② Send PCS shutdown. ③ Disconnect AC and DC circuit breakers.
52 |  | BMU fan fault | / | ① Enable alarm light
53 |  | BMU thermal runaway alarm | ① Set the charging and discharge limit current to 0. ② Output DO to shut down PCS. ③ Self-recovery is not allowed; disconnect the DC circuit breaker when LC communication loss fault is triggered. | ① Enable alarm light, start audio-visual alarm, and start remote emergency stop. ② Send PCS shutdown. ③ Air conditioner shutdown ④ Exhaust fan runs at full speed, and BMU fan operates synchronously. ⑤ Disconnect AC and DC circuit breakers.
55
56
0.1 | Alarm | Cell undervoltage alarm | / | /
2 |  | Total undervoltage alarm | / | /
3 |  | Cell overvoltage alarm | / | /
4 |  | Total overvoltage alarm | / | /
5 |  | Charging overtemperature alarm | / | /
6 |  | Discharge overtemperature alarm | / | /
7 |  | Charging overcurrent alarm | / | /
8 |  | Discharge overcurrent alarm | / | /
9 |  | Charging low temperature alarm | / | /
0.1 |  | Discharge low temperature alarm | / | /
0.10.1 |  | Excessive differential pressure alarm | / | /
0.12 |  | Excessive temperature difference alarm | / | /
0.13 |  | BMS power connector overtemperature alarm | / | ① Enable alarm light
0.14 |  | BMU power connector overtemperature alarm | / | /
0.15 |  | Insulation alarm | / | /
0.16 |  | Power supply voltage abnormal alarm | / | /
0.17 |  | BMU version abnormal | / | /
0.18 |  | Insulation Self-check in Progress | / | ① Alarm light on ② Send PCS shutdown; if there is still power with an absolute value greater than 0.0.1kw for more than 6s after output is shut down, disconnect the DC circuit breaker.
0.19
20
20.1
22
23
24
25
26
27
28
29
30
30.1
32

## PCS Fault Summary
+
No. | Fault Type | Fault Name | Corresponding PCS Actions | Corresponding LC Actions | Remarks
1 | Protection | F01 PV input reverse connection fault 1 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. | PCS shuts down due to a fault, and MPPT shuts down synchronously.
2 |  | F02 auxiliary microcontroller fault 2 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
3 |  | STS disconnection | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
4 |  | Parallel ID conflict | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
5 |  | F05 read/write memory error 5 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
6 |  | F06 write memory error 6 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
7 |  | F07 DCDC startup failure 7 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
8 |  | F08 GFDI (battery end grounded) grounding contactor fault 8 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
9 |  | PCS to LC communication lost | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
10 |  | F10 auxiliary switch power fault (auxiliary switch power 10) | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
11 |  | F11 AC main contactor error 11 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
12 |  | F12 AC auxiliary contactor error 12 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
13 |  | F13 reserved 13 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
14 |  | F14 DC software overcurrent fault 14 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
15 |  | F15 AC software overcurrent fault 15 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
16 |  | F16 GFCI (RCD) AC leakage current fault 16 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
17 |  | F17 PV hardware overcurrent fault 17 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
18 |  | F18 AC hardware overcurrent fault 18 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
19 |  | F19 hardware integration fault 19 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
20 |  | F20 DC hardware overcurrent fault 20 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
21 |  | F21 DC leakage current overcurrent fault 21 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
22 |  | F22 emergency stop fault 22 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
23 |  | F23 AC leakage current instantaneous overcurrent fault 23 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
24 |  | F24 DC insulation resistance fault 24 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
25 |  | F25 DC backfeed fault 25 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
26 |  | F26 DC bus unbalance fault 26 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
27 |  | F27 balance bridge arm overcurrent 27 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
28 |  | F28 inverter 128 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
29 |  | F29 AC load switch fault 29 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
30 |  | F30 AC main contactor fault 30 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
31 |  | F31 AC auxiliary contactor fault 31 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
32 |  | F32 Inverter 232 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
33 |  | F33 AC current too high (AC overcurrent fault reported by software, 133) | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
34 |  | F34 AC overload 34 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
35 |  | F35 AC side no mains power error 35 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
36 |  | F36 AC grid phase sequence error 36 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
37 |  | F37 AC three-phase voltage imbalance fault 37 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
38 |  | F38 AC three-phase current imbalance fault 38 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
39 |  | F39 AC overcurrent fault (overcurrent fault reported by software, within one switching cycle) 39 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
40 |  | F40 DC overcurrent fault 40 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
41 |  | F41 AC WU41 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
42 |  | F42 AC WU42 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
43 |  | F43 AC VW43 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
44 |  | F44 AC VW44 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
45 |  | F45 AC UV45 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
46 |  | STS module error | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
47 |  | F47 AC frequency too high fault 47 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
48 |  | F48 AC frequency too low fault 48 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
49 |  | F49 phase grid-connected current DC component high 49 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
50 |  | F50 battery overcurrent 50 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
51 |  | F51 battery temperature too high 51 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
52 |  | F52 battery voltage too high 52 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
53 |  | F53 battery auxiliary relay fault 53 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
54 |  | F54 battery main relay fault 54 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
55 |  | F55 DC bus overvoltage fault 55 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
56 |  | F56 DC bus undervoltage fault 56 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
57 |  | F57 AC backfeed fault 57 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
58 |  | F58 BMS communication fault 58 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
59 |  | F59 battery overcurrent fault 59 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
60 |  | F60 AC grid W current overcurrent fault 60 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
61 |  | F61 manual shutdown of inverter 61 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
62 |  | F62 Australia DRM62 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
63 |  | F63 arc fault 63 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
64 |  | F64 inverter temperature too high 64 | ① PCS displays the fault status. ② PCS internal relay disconnects. | ① Enable alarm light. PCS actively shuts down. ② If there is still power with an absolute value greater than 0.1kw for more than 6s after PCS actively shuts down, disconnect the AC circuit breaker. ③ After a fault occurs, if the PCS actively shuts down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.

## MPPT Fault Summary
MPPT Fault Summary
No. | Fault Type | Fault Name | Corresponding PCS Actions | Corresponding LC Actions | Remarks
1 | Protection | PV input reverse connection fault 1 | / | ① Enable alarm light
2 |  | Auxiliary microcontroller fault 2 | / | ① Enable alarm light
3 |  | DC leakage current fault 3 | / | ① Enable alarm light
4 |  | GFDI (battery end grounded) grounding fault 4 | / | ① Enable alarm light
5 |  | Read/write memory error 5 | / | ① Enable alarm light
6 |  | Write memory error 6 | / | ① Enable alarm light
7 |  | DCDC startup failure 7 | / | ① Enable alarm light
8 |  | GFDI (battery end grounded) grounding contactor fault 8 | / | ① Enable alarm light
9 |  | Boost circuit fault | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
10 |  | Auxiliary power supply fault (auxiliary power supply 10) | / | ① Enable alarm light
11 |  | AC main contactor error 11 | / | ① Enable alarm light
12 |  | AC auxiliary contactor error 12 | / | ① Enable alarm light
13 |  | Reserved 13 | / | ① Enable alarm light
14 |  | Software overcurrent | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
15 |  | AC software overcurrent fault 15 | / | ① Enable alarm light
16 |  | GFCI (RCD) AC leakage current fault 16 | / | ① Enable alarm light
17 |  | PV hardware overcurrent fault 17 | / | ① Enable alarm light
18 |  | AC hardware overcurrent fault 18 | / | ① Enable alarm light
19 |  | Hardware overvoltage and undervoltage | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
20 |  | Hardware overcurrent | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
21 |  | DC leakage current overcurrent fault 21 | / | ① Enable alarm light
22 |  | Emergency stop fault 22 | / | ① Enable alarm light
23 |  | AC leakage current instantaneous overcurrent fault 23 | / | ① Enable alarm light
24 |  | Insulation resistance fault | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
25 |  | DC backfeed fault 25 | / | ① Enable alarm light
26 |  | DC bus unbalance fault 26 | / | ① Enable alarm light
27 |  | Balance bridge arm overcurrent 27 | / | ① Enable alarm light
28 |  | Inverter 128 | / | ① Enable alarm light
29 |  | AC load switch fault 29 | / | ① Enable alarm light
30 |  | Main relay open/short circuit | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
31 |  | Precharging relay fault | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
32 |  | Inverter 232 | / | ① Enable alarm light
33 |  | AC current too high (AC overcurrent fault reported by software, 133) | / | ① Enable alarm light
34 |  | AC overload 34 | / | ① Enable alarm light
35 |  | AC side no mains power error 35 | / | ① Enable alarm light
36 |  | AC grid phase sequence error 36 | / | ① Enable alarm light
37 |  | AC three-phase voltage imbalance fault 37 | / | ① Enable alarm light
38 |  | AC three-phase current imbalance fault 38 | / | ① Enable alarm light
39 |  | AC overcurrent fault (overcurrent fault reported by software, within one switching cycle) 39 | / | ① Enable alarm light
40 |  | DC overcurrent fault 40 | / | ① Enable alarm light
41 |  | AC WU41 | / | ① Enable alarm light
42 |  | AC WU42 | / | ① Enable alarm light
43 |  | AC VW43 | / | ① Enable alarm light
44 |  | AC VW44 | / | ① Enable alarm light
45 |  | AC UV45 | / | ① Enable alarm light
46 |  | AC UV46 | / | ① Enable alarm light
47 |  | AC overfrequency fault 47 | / | ① Enable alarm light
48 |  | AC underfrequency fault 48 | / | ① Enable alarm light
49 |  | Phase grid-connected current DC component high 49 | / | ① Enable alarm light
50 |  | Battery overcurrent 50 | / | ① Enable alarm light
51 |  | Battery temperature too high 51 | / | ① Enable alarm light
52 |  | Battery voltage too high 52 | / | ① Enable alarm light
53 |  | Battery auxiliary relay fault 53 | / | ① Enable alarm light
54 |  | Battery main relay fault 54 | / | ① Enable alarm light
55 |  | DC bus overvoltage | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.
56 |  | DC bus undervoltage fault 56 | / | ① Enable alarm light
57 |  | AC backfeed fault 57 | / | ① Enable alarm light
58 |  | BMS communication fault 58 | / | ① Enable alarm light
59 |  | Battery overcurrent fault 59 | / | ① Enable alarm light
60 |  | AC grid W current overcurrent fault 60 | / | ① Enable alarm light
61 |  | Manual shutdown of inverter 61 | / | ① Enable alarm light
62 |  | Australia DRM 62 | / | ① Enable alarm light
63 |  | Arc fault 63 | / | ① Enable alarm light
64 |  | Temperature too high or too low | ① MPPT displays fault status ② MPPT stops working | ① Enable alarm light ② MPPT stops working, and inverter operates normally. ③ If MPPT has output power for more than 3s, the inverter shuts down. ④ If the output inverter shuts down and the PV side still has power with an absolute value greater than 0.5kw for more than 6s, disconnect the DC circuit breaker.

## STS Fault Summary
STS Fault Summary
No. | Fault Type | Fault Name | Corresponding PCS Actions | Corresponding LC Actions | Remarks
1 | Protection | PV input reverse connection fault 1 | / | ① Enable alarm light
2 |  | Auxiliary microcontroller fault 2 | / | ① Enable alarm light
3 |  | STS disconnection | / | ① Enable alarm light
4 |  | GFDI (battery end grounded) grounding fault 4 | / | ① Enable alarm light
5 |  | Read/write memory error 5 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
6 |  | Write memory error 6 | / | ① Enable alarm light
7 |  | DCDC startup failure 7 | / | ① Enable alarm light
8 |  | Inverter startup failure 8 | / | ① Enable alarm light
9 |  | STS to LC communication lost | / | ① Enable alarm light
10 |  | Auxiliary power supply fault (auxiliary power supply 10) | / | ① Enable alarm light
11 |  | AC main contactor error 11 | / | ① Enable alarm light
12 |  | AC auxiliary contactor error 12 | / | ① Enable alarm light
13 |  | Reserved 13 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
14 |  | DC software overcurrent fault 14 | / | ① Enable alarm light
15 |  | AC software overcurrent fault 15 | / | ① Enable alarm light
16 |  | GFCI (RCD) AC leakage current fault 16 | / | ① Enable alarm light
17 |  | PV hardware overcurrent fault 17 | / | ① Enable alarm light
18 |  | AC hardware overcurrent fault 18 | / | ① Enable alarm light
19 |  | Hardware integration fault 19 | / | ① Enable alarm light
20 |  | DC hardware overcurrent fault 20 | / | ① Enable alarm light
21 |  | DC leakage current overcurrent fault 21 | / | ① Enable alarm light
22 |  | Emergency stop fault 22 | / | ① Enable alarm light
23 |  | AC leakage current instantaneous overcurrent fault 23 | / | ① Enable alarm light
24 |  | DC insulation resistance fault 24 | / | ① Enable alarm light
25 |  | DC backfeed fault 25 | / | ① Enable alarm light
26 |  | DC bus unbalance fault 26 | / | ① Enable alarm light
27 |  | Balance bridge arm overcurrent 27 | / | ① Enable alarm light
28 |  | Inverter 128 | / | ① Enable alarm light
29 |  | AC load switch fault 29 | / | ① Enable alarm light
30 |  | AC main contactor fault 30 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
31 |  | AC auxiliary contactor fault 31 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
32 |  | Inverter 232 | / | ① Enable alarm light
33 |  | AC current too high (AC overcurrent fault reported by software, 133) | / | ① Enable alarm light
34 |  | AC overload 34 | / | ① Enable alarm light
35 |  | AC side no mains power error 35 | / | ① Enable alarm light
36 |  | AC grid phase sequence error 36 | / | ① Enable alarm light
37 |  | AC three-phase voltage imbalance fault 37 | / | ① Enable alarm light
38 |  | AC three-phase current imbalance fault 38 | / | ① Enable alarm light
39 |  | AC overcurrent fault (overcurrent fault reported by software, within one switching cycle) 39 | / | ① Enable alarm light
40 |  | DC overcurrent fault 40 | / | ① Enable alarm light
41 |  | AC WU41 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
42 |  | AC WU42 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
43 |  | AC VW43 | / | ① Enable alarm light
44 |  | Off-grid loss of control panel communication | / | ① Enable alarm light
45 |  | AC UV45 | / | ① Enable alarm light
46 |  | AC UV46 | / | ① Enable alarm light
47 |  | AC overfrequency fault 47 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
48 |  | AC underfrequency fault 48 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
49 |  | Phase grid-connected current DC component high 49 | / | ① Enable alarm light
50 |  | Battery overcurrent 50 | / | ① Enable alarm light
51 |  | Battery temperature too high 51 | / | ① Enable alarm light
52 |  | Battery voltage too high 52 | / | ① Enable alarm light
53 |  | Battery auxiliary relay fault 53 | / | ① Enable alarm light
54 |  | Battery main relay fault 54 | / | ① Enable alarm light
55 |  | DC bus overvoltage fault 55 | / | ① Enable alarm light
56 |  | DC bus undervoltage fault 56 | / | ① Enable alarm light
57 |  | AC backfeed fault 57 | / | ① Enable alarm light
58 |  | BMS communication fault 58 | / | ① Enable alarm light
59 |  | Battery overcurrent fault 59 | / | ① Enable alarm light
60 |  | AC grid W current overcurrent fault 60 | / | ① Enable alarm light
61 |  | Manual shutdown of inverter 61 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.
62 |  | Australia DRM 62 | / | ① Enable alarm light
63 |  | Arc fault 63 | / | ① Enable alarm light
64 |  | Inverter temperature too high 64 | ① STS displays fault status. ② STS stops working | ① Enable alarm light ② If there is still power with an absolute value greater than 0.1kw for more than 6s after the output is shut down, disconnect the AC circuit breaker. ③ After a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker.

## Air Conditioner Fault Summary
Air Conditioner Fault Summary
No. | Fault Type | Fault Name | Corresponding Air Conditioner Actions | Corresponding LC Actions | Remarks
1 | Protection | High temperature alarm |  | /
2 |  | Low temperature alarm |  | /
3 |  | High humidity alarm |  | /
4 |  | Low humidity alarm |  | / | Prone to false alarms, cancel
5 |  | Electric heater protection |  | /
6 |  | Outdoor environment temperature fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side. | PCS shuts down due to a fault, and MPPT shuts down synchronously.
7 |  | External coil temperature fault |  | /
8 |  | Exhaust temperature fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
9 |  | Internal ambient temperature 1 fault |  | /
10 |  | Internal ambient temperature 2 fault |  | ① Web display | G230 does not have this fault.
11 |  | Internal ambient humidity 1 fault |  | /
12 |  | Internal ambient humidity 2 fault |  | ① Web display | G230 does not have this fault.
13 |  | Internal coil temperature fault |  | /
14 |  | Pressure sensor failure | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
15 |  | Exhaust temperature overheat protection | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
16 |  | Outer coil temperature protection |  | /
17 |  | Internal coil temperature protection |  | /
18 |  | Internal fan failure |  | /
19 |  | Internal fan communication fault |  | /
20 |  | Internal fan overload fault |  | /
21 |  | External fan failure |  | /
22 |  | External fan communication fault |  | /
23 |  | External fan overload fault |  | /
24 |  | Compressor startup fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
25 |  | Compressor communication fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
26 |  | Indoor temperature sensor 1 and sensor 2 fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
27 |  | Indoor humidity sensor 1 and sensor 2 fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
28 |  | Water level switch protection | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
29 |  | Low-voltage switch protection | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
30 |  | Air conditioner high pressure too high fault | ① Shutdown | ① Enable alarm light ② Send air conditioner shutdown command. ③ Send PCS shutdown; after a fault occurs, if the output is shut down but the absolute value of the DC side current is still greater than 2A for a cumulative duration exceeding 10s, disconnect the DC circuit breaker. ④ Send PCS shutdown; if there is still 0.1kW feeding to the grid for more than 6s after PCS shuts down, trip the AC side.
31
32
33
34
35
36
37
38
39
40
41
42
43

## Environmental Fault Summary
Environmental Faults (LC)
No. | Test Item | Corresponding Actions | Expected Phenomenon | Remarks
1 | Light/voice test | No fault trigger, BMS terminal alarm | Operation light on, alarm light off | Priority 3
|  | DI1 emergency stop feedback (high level trigger) DI4 water infiltration feedback (low level trigger) DI5 aerosol feedback (low level trigger) DI6 battery compartment access control (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback (high level trigger) DI10 electrical compartment access control (low level trigger) DI11 lightning protection signal feedback (high level trigger) DI13 temperature sensor feedback (low level trigger) DI14 smoke sensor feedback (low level trigger) Fire alarm (temperature sensor + smoke sensor) AC air conditioner communication lost BMS communication lost PCS communication lost Transformer-side electricity meter communication lost PCS, BMS, air conditioner, MPPT secondary fault Single pack thermal runaway Fire protection feedback (aerosol spray) fault QF1 AC circuit breaker control failure QF2 DC circuit breaker control failure MPPT communication lost CPU core 1 temperature abnormal CPU core 2 temperature abnormal CPU core 3 temperature abnormal PCS startup failure | Alarm light on, operation light off | Priority 1
|  | LC does not issue a limit-power-to-0 command, does not issue a shutdown command, and the PCS is currently in the on state with no faults: Electricity meter 1 communication lost Electricity meter 2 communication lost Dehumidifier communication lost Solid state drive mounting lost Abnormal loss of historical database DI7 gas low alarm (low level trigger) Gas sensor communication lost Dehumidifier fan module circuit fault Dehumidifier dehumidification module circuit fault Dehumidifier humidity sensor status abnormal alarm Dehumidifier external temperature sensor status abnormal alarm Dehumidifier internal temperature sensor status abnormal alarm Dehumidifier high temperature alarm DI10 electrical compartment access control (low level trigger) Inverter LCD panel communication lost | Operation light on, fault light on | Priority 2
2 | Exhaust fan test | DI7 gas low alarm (low level trigger) DI8 gas high alarm (low level trigger) DI13 temperature sensor feedback DI14 smoke sensor feedback Fire alarm (temperature sensor + smoke sensor) Maximum battery cell temperature ≥ 65℃ DI5 aerosol feedback (low level trigger) Single pack thermal runaway DI9 electrical compartment aerosol feedback (high level trigger) Fire protection feedback (aerosol spray) fault | Exhaust fan starts
|  | Once the maximum battery cell temperature reaches or drops below 45°C, all temperature acquisitions are normal. After the DI7 low alarm is cleared, continue exhausting for 30 minutes. | Exhaust fan stops
|  | DI6 battery compartment access control (low level trigger) | Exhaust fan stops
3 | PACK fan test | Start synchronously with the exhaust fan. | PACK fan starts
|  | After the exhaust fan stops, the PACK fan runs automatically as usual. | PACK fan runs automatically as usual
|  | BMU communication is lost. | PACK fan runs at 70% speed
|  | DI6 battery compartment access control (low level trigger) | PACK fan stops
4 | Audio-visual test | DI5 aerosol feedback (low level trigger) Fire alarm (temperature sensor + smoke sensor) DI13 temperature sensor feedback (low level trigger) DI14 smoke sensor feedback (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback Single pack thermal runaway Fire protection feedback (aerosol spray) fault Smoke or temperature sensor reports to LC, and LC reports to the fire alarm control panel through IO board DO2 (temperature sensor) and DO3 (smoke sensor). If the fire alarm control panel does not respond within 30s (IO board DI3 (audio-visual input)), LC starts executing an audio-visual alarm.. | Audio-visual start
5 | Remote emergency stop test | DI4 water infiltration feedback (low level trigger) DI5 aerosol feedback (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback Fire alarm (temperature sensor + smoke sensor) Single pack thermal runaway Fire protection feedback (aerosol spray) fault | Remote emergency stop activated
6 | Aerosol 1 spray test | Fire alarm (temperature sensor + smoke sensor) or (smoke sensor + thermal runaway) Smoke sensor or temperature sensor reports to LC, and LC reports to the fire alarm control panel through IO board DO2 (temperature sensor) and DO3 (smoke sensor). If the fire alarm control panel does not respond within 30s (IO board DI4 (aerosol input)), LC starts executing aerosol. | Aerosol 1 spray | Aerosol not controlled
7 | PCS shutdown test | DI1 emergency stop feedback (high level trigger) DI4 water infiltration feedback (low level trigger) DI5 aerosol feedback (low level trigger) DI6 battery compartment access control (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback Fire alarm (temperature sensor + smoke sensor) DI13 temperature sensor feedback (low level trigger) DI14 smoke sensor feedback (low level trigger) Single pack thermal runaway Fire protection feedback (aerosol spray) fault | PCS shutdown
8 | Air conditioner shutdown test | DI1 emergency stop feedback (high level trigger) DI5 aerosol feedback (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback Fire alarm (temperature sensor + smoke sensor) DI13 temperature sensor feedback (low level trigger) DI14 smoke sensor feedback (low level trigger) DI4 water infiltration feedback (low level trigger) Single pack thermal runaway Single pack fire protection fault | Air conditioner shutdown
9 | Circuit breaker trip test | DI1 emergency stop feedback (high level trigger) DI4 water infiltration feedback (low level trigger) DI5 aerosol feedback (low level trigger) DI8 gas high alarm (low level trigger) DI9 electrical compartment aerosol feedback Fire alarm (temperature sensor + smoke sensor) Single pack thermal runaway Fire protection feedback (aerosol spray) fault | QF1 Trip
QF2 Trip
Environmental fault (LC expansion board)
No. | Test Item | Corresponding Actions | Expected Phenomenon | Remarks
| DO1 generator start/stop | When the energy storage cabinet SOC is less than the generator start SOC, the diesel generator starts. When the energy storage cabinet SOC is greater than the generator shutdown SOC, the diesel generator stops. |  | DI3 audio-visual input DI4 aerosol start input DI5 emergency signal input (synchronized with "emergency stop" strategy) DI6 exhaust valve feedback DI7 exhaust valve 1 feedback DI8 exhaust valve 2 feedback
| DO2 temperature sensor output | DI13 temperature sensor feedback, output high level
| DO3 smoke sensor output | DI14 smoke sensor feedback, output high level
| DO4 PCS fan | Either PCS temperature 1 or PCS temperature 2 is greater than 45℃.
| DO5 MPPT fan | Turn on when MPPT heatsink temperature is greater than 55℃ and off when less than 45℃.
| DO6 exhaust valve switch | Synchronized with the "exhaust fan" strategy
Environmental fault (STS expansion board)
No. | Test Item | Corresponding Actions | Expected Phenomenon | Remarks
| DO1 grid circuit breaker trip | Synchronized with the "fire alarm (temperature sensor + smoke sensor)" strategy |  | DI1 grid circuit breaker feedback DI2 generator circuit breaker feedback DI3 lightning protection feedback
| DO2 generator circuit breaker trip | Synchronized with the "fire alarm (temperature sensor + smoke sensor)" strategy

## Dehumidifier Fault Summary
Dehumidifier Fault Summary
No. | Fault Type | Fault Name | Corresponding Dehumidifier Actions | Corresponding LC Actions | Remarks
1 |  | Dehumidifier fan module circuit fault | ① Dehumidifier shutdown | ① Operation light on, fault light on
2 |  | Dehumidifier dehumidification module circuit fault | ① Dehumidifier shutdown | ① Operation light on, fault light on
3 |  | Dehumidifier humidity sensor status abnormal alarm |  | ① Operation light on, fault light on
4 |  | Dehumidifier external temperature sensor status abnormal alarm |  | ① Operation light on, fault light on
5 |  | Dehumidifier internal temperature sensor status abnormal alarm |  | ① Operation light on, fault light on
6 |  | Dehumidifier high temperature alarm |  | ① Operation light on, fault light on

## Diesel Generator Fault Summary
Diesel Generator Fault Summary
No. | Fault Type | Fault Name | Corresponding Dehumidifier Actions | Corresponding LC Actions | Remarks
1 |  | Emergency Stop
2 |  | Engine low oil pressure | ① Generator shutdown
3 |  | Engine high water temperature | ① Generator shutdown
4 |  | Engine low water temperature
5 |  | Low speed | ① Generator shutdown
6 |  | Overspeed | ① Generator shutdown
7 |  | Generator low frequency | ① Generator shutdown
8 |  | Generator overfrequency | ① Generator shutdown
9 |  | Generator low voltage | ① Generator shutdown
10 |  | Generator overvoltage | ① Generator shutdown
11 |  | Battery low voltage
12 |  | Battery high voltage
13 |  | Charging generator failure
14 |  | Startup failure
15 |  | Shutdown failure
16 |  | Generator closing failure
17 |  | Mains power closing failure
18 |  | Oil pressure sensor fault
19 |  | Rotation speed sensor signal lost
20 |  | Rotation speed sensor open circuit
21 |  | Overcurrent | ① Generator shutdown
22 |  | Low oil level
23 |  | CAN ECU alarm
24 |  | CAN ECU shutdown
25 |  | CAN ECU data communication failure
26 |  | Low engine oil level switching value
27 |  | High water temperature switching value
28 |  | Low fuel level switching value
29 |  | Expansion module watchdog alarm
30 |  | Overload alarm | ① Generator shutdown
31 |  | Maintenance alarm
32 |  | On-load frequency alarm
33 |  | On-load voltage alarm
34 |  | ECU protection
35 |  | ECU
36 |  | ECU shutdown
37 |  | ECU alarm
38 |  | ECU trip

## EMS Fault Summary
EMS Fault Summary
No. | Fault Type | Fault Name | Fault Code | Corresponding Actions of Other Energy Storage Cabinets | Remarks
1 | Protection | EMS fire fault (Smoke sensor + temperature sensor, battery pack, battery compartment, electrical compartment aerosol spray) | 2 | ① Enable alarm light ② QF1, QF2 trip ③ Air conditioner shutdown ④ PCS, MPPT shutdown | Non-recoverable
2 |  | EMS remote emergency stop (External input) | 2 | ① Enable alarm light ② PCS, MPPT shutdown ③ Air conditioner shutdown
3 |  | EMS STS communication lost | 2 | ① Enable alarm light ② The PCS is currently fault-free and has remained so for 5 minutes, only then can it be determined that the PCS and MPPT have shut down.
4 |  | EMS STS cabinet electricity meter communication lost | 1 | /
5 |  | EMS STS cabinet IO board communication lost | 1 | /
6 |  | EMS STS cabinet dehumidifier communication lost | 1 | /
7 |  | EMS diesel generator communication lost | 1 | /
8 |  | EMS grid signal feedback | 1 | /
9 |  | EMS diesel generator feedback | 1 | /
10 |  | EMS lightning protection module alarm | 1 | /
11 |  | EMS solid state drive mounting lost | 2 | ① Enable alarm light ② PCS, MPPT shutdown
12 |  | EMS 4G module mounting lost | 2 | ① Enable alarm light ② PCS, MPPT shutdown
13 |  | Abnormal loss of EMS historical database | 2 | ① Enable alarm light ② PCS, MPPT shutdown
14 |  | EMS CPU core 1 temperature abnormal | 2 | ① Enable alarm light ② PCS, MPPT shutdown
15 |  | EMS CPU core 2 temperature abnormal | 2 | ① Enable alarm light ② PCS, MPPT shutdown
16 |  | EMS CPU core 3 temperature abnormal | 2 | ① Enable alarm light ② PCS, MPPT shutdown